## Sheet1
Electrical Works
Panel Boards
Panel GLP Main: 3P-100AT, 150AF, 230V, 18KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch: 22-20AT, loatw, 2P, 10KA1C 2-20AT, 100AF, 2P, IOKAIC(SPARE) | 1 | assy
Panel GPP1 Main: 3P-125AT, 150AF, 230V, 18KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK Branch: 29-20AT, 100AF, 2P, 10KAIC FOR SOLID GROUND 1-20AT, 100AF, 2P, 10KAIC(SPARE) | 1 | assy
Panel GPP2 Main: 3P-175A1 225AF, 230V, 22KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK Branch: 22-20AT, 100AF, 2P, 10KAIC FOR SOLID GROUND Branch: 22-20AT, 100AF, 2P, 10KAIC 2-20AT, 100AF, 2P, 10KAIC(SPARE) 1-125AT, 150AF, 3P, 18KAIC 1-125AT, 150AF, 3P, 18KAIC | 1 | assy
Panel GPP3 Main : 3P-250.4T, 250AF, 230V, 22KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 24-20AT, IOOAF, 2P, 101C41C Branch : 24-20AT, IOOAF, 2P, 101C41C 1-100AT, 150AF, 3P, 18KAIC | 1 | assy
Panel 2PP1,3PP1.„4PPI Main :3P-100AT, 150AF, 230V, 18KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch :21-20AT, 100AF, 2P, 10KAIC 3-20AT, IOOAF, 2P, IOKAIC(SPARE) 3-20AT, IOOAF, 2P, IOKAIC(SPARE) | 3 | assy
PaneL, 2PP2,3PP2,4PP2 Main : 3P-175AT, 225AF, 230V, 22KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch :22-20AT, IOOAF, 2P, 10KAIC 2-20AT,100AF, 2P, 10KAIC(SPARE) 1-100AT, 150AF, 3P, 18KAIC | 3 | assy
Panel 2LP,3LPALP Main : 3P-70AT, 150AF, 230V, 18KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL Branch : 11-20AT, 100AF, 2P, 10KAIC BLOCK FOR SOLID GROUND 1-20AT, 100AF, 2P, 10KAIC(SPARE) 1-20AT, 100AF, 2P, 10KAIC(SPARE) | 3 | assy
Panel 2PP3,3PP3,4PP3 Main : 3P-225AT, 250AF, 230V, 22KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 24-20AT, 100AF, 2P, 10KA1C 1-50AT, 150AF, 3P, 18KAIC | 3 | assy
Panel RLP Main :3P-50AT, 150AF, 230V, 18KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 5-20AT, 100AF, 2P, 10KAIC 1-20AT, 100.4F, 2P, 10KAIC(SPARE) | 1 | assy
Panel GLPE Main : 3P-40AT, 100AF, 230V, I8KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 11-20AT, 100AF, 2P, 10KA1C 1-20AT, 100AF, 2P, 10KAIC(SPARE) 1-20AT, 100AF, 2P, 10KAIC(SPARE) | 1 | assy
Panel 2LPE,3LPE,4LPE Main: 3P-30AT, 100AF, 2301, 18KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 5-20AT, 100AF, 2P, 18KAIC 1-20AT, 100AF, 2P, 18KAIC(SPARE) | 3 | assy
Panel MDPE Main: 3P-150AT, 225AF, 230V, 2201C MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 1-100AT, 123AF, 3P, 10KAIC 1-40AT, 100AF, 3P, 10KAK 4-30AT, 100AF, 3P, 10KAIC 2-30AT, 100AF, 3P, 10KAIC(SPARE) | 1 | assy
Panel LAP Main: 3P-IOOAT, 150AF; 230V, I8KAIC MCCB TYPE FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch : 11-20AT, 100AF, 2P, 10KAIC 1-204T, 100AF, 2P, 10KAIC(SPARE) | 1 | assy
Panel MDP Main: 3P-1500AT, 1600AF, 230V, 42KAIC MCCB TYPE NEMA 1, SURFACE MOUNTED WITH GRAY POWDERED PAINT FINISH WITH MULTI-TERMINAL BLOCK FOR SOLID GROUND Branch :1-600AT, 600AF, 3P, 42KAIC 1-250AT, 250AF, 3P, 22KAIC 3-225AT, 250AF, 3P, 22KAIC 4-175AT, 225AF, 3P, 22KAIC 1-150AT, 225AF, 312, 22KAIC 1-100AT, 150AF, 3P, 18KAIC 2-50AT, 150AF, 3P, 18KAIC 1-50AT, 150AF, 3P, 181071C(SPARE) | 1 | assy
ATS 160AT,3P Nema3R | 1 | assy
Automatic transfer switch 3Phase ATS 600 AT | 1 | Set
3 Phase ECB 100AT | 1 | Set
3 Phase ECB 40AT | 1 | Set
3 Phase ECB 30AT | 1 | Set
Wires
THHN wire 3.5 mm2 | 600 | Boxes
THHN wire 5.5 mm2 | 4 | Boxes
THHN wire 8.0 mm2 | 4 | Boxes
THHN wire 14.0 mm2 | 2 | Boxes
THHN wire 22.0 mm2 | 3 | Boxes
THHN wire 30.0 mm2 | 3 | Boxes
THHN wire 38.0 mm2 | 860 | m
THHN wire 60.0 mm2 | 510 | m
THHN wire 100.0 mm2 | 266 | m
THHN wire 125.0 mm2 | 136 | m
THHN wire 200.0 mm2 | 1506 | m
#50 sq THW Copper Wire | 160 | Mtrs
#30mm sqTW Copper cable | 80 | Mtrs
50mm dia Upvc conduit | 16 | Lgts
50mm dia Upvc conduit clamp | 80 | Pcs
50mm dia bushing and locknut | 16 | Pcs
4’X18”x18” fabricated gutter Box | 4 | Pcs
Pipes
Conduit 20mm dia PVC | 12 | Pcs
Conduit 32mm dia PVC | 7 | Pcs
Conduit 65mm dia PVC | 11 | Pcs
Conduit 100mm dia PVC | 145 | Pcs
Grounding rods 20mm X 3000mm | 12 | Pcs
Grounding rods 15mm X 3000mm | 1 | Pcs
15mm diameter IMC PIPE | 25 | pcs
20mm diameter IMC PIPE | 20 | pcs
25mm diameter IMC PIPE | 80 | pcs
32mm diameter IMC PIPE | 25 | pcs
50mm diameter IMC PIPE | 52 | pcs
65mm diameter IMC PIPE | 20 | pcs
80mm diameter IMC PIPE | 4 | pcs
100mm diameter IMC PIPE | 30 | pcs
65mm PVC pipe | 14 | pcs
20mm PVC Pipe | 2975 | pcs
Fittings/Boxes | 1 | pcs
Hangers & Supports | 1 | pcs
Lighting
Light fixtures (1x40-boxtype) daylight | 400 | Pcs
Pin lights (4’) daylights | 500 | Pcs
Emergency lights | 32 | Pcs
Outlet for Emergency | 32 | Pcs
Utility box | 202 | Pcs
Troffer lights assembly | 40 | Pcs
Switch 2 gang | 160 | Pcs
Switch 1-gang | 144 | Pcs
3-way switch, 2-gang | 16 | Pcs
One-gang switch; 300VAC, 15A | 128 | pcs
Three-gang switch; 300VAC, 15A | 15 | pcs
Three-way Two-gang switch; for RS | 16 | pcs
2 X 40 Luminaire with aluminum reflector Surface Type LED | 349 | assy
Switchbank 2DB | 4 | pcs
Power
Convenience outlet 1 gang | 810 | Pcs
Convenience outlet 2 gang | 260 | Pcs
Convenience outlet (WP) weather proof | 5 | Pcs
GFCI outlet 2-gang (WP) weather proof | 16 | Pcs
Utility Box | 1130 | Pcs
Receptacle outlets
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps | 548 | pcs
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps; for CH | 464 | pcs
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps; for iron | 116 | pcs
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps, GFCI; for CH | 32 | pcs
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps; for HD | 16 | pcs
Single convenience outlet, 16A, 250V,parallel slots, grounding type; for water heater | 84 | pcs
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps; WP | 4 | pcs
duplex convenience outlet, 3-prong, universal slots grounding type, 15amps, GFCI; for WP | 18 | pcs
Miscellaneous
Heater 3500 watts | 80 | Pcs
Hand dryer 1800 Watts | 4 | Pcs
Outlet for heater & dryer 1 gang | 84 | Pcs
Emergency Exit signs board with LED lights and Accessories | 8 | Sets
Utility Box | 84 | Pcs
Generator Set
125kW, 230V AC, 60hz silent type stand-by genset Diesel generator | 1 | Set